## Approved_Calibration
NBP2 Instrument Calibration and Offsets
Approved calibration records. Apply these corrections to exported historian values before engineering calculations.
Instrument | Measurement | Approved record | Calibration date | Historian / indicated issue | Approved correction formula | Valid for assessment | Authority note
FT-210 | Booster discharge flow | CAL-FT210-2026-0418 | 2026-04-18 | DCS historian mapping remained at 0-200 m3/h after transmitter was re-ranged to 0-250 m3/h. | Corrected flow = historian indicated flow x 1.25 | Yes | Signed calibration certificate; overrides historian tag description.
PT-401 | Pump suction pressure | CAL-PT401-2026-0421 | 2026-04-21 | Transmitter indicates 0.15 bar higher than reference gauge across operating range. | Corrected suction pressure = indicated pressure - 0.15 bar | Yes | Use for event reconstruction and NPSH cross-check.
PT-404 | Packaging-hall pressure | CAL-PT404-2026-0421 | 2026-04-21 | Transmitter indicates 0.12 bar higher than reference gauge across operating range. | Corrected hall pressure = indicated pressure - 0.12 bar | Yes | Use for minimum-pressure compliance.
LT-201 | Source tank liquid level relative to pump centreline | CAL-LT201-2026-0419 | 2026-04-19 | Level transmitter agrees with manual dip within +/-0.03 m. | Corrected level = indicated level | Yes | No level correction required.

## Superseded_Records
Superseded Calibration Records
These records remain in the file set to create deliberate conflicts. They must not be used for the final assessment.
Record | Instrument | Date | Superseded claim | Why superseded | Replacement record
CAL-FT210-2025-1110 | FT-210 | 2025-11-10 | Historian flow values may be used without correction. | FT-210 was re-ranged in April 2026 and the DCS mapping was not updated. | CAL-FT210-2026-0418
CAL-PT401-2025-0908 | PT-401 | 2025-09-08 | No suction-pressure offset required. | April 2026 calibration found positive bias of 0.15 bar. | CAL-PT401-2026-0421
CAL-PT404-2025-0908 | PT-404 | 2025-09-08 | Subtract 0.02 bar from indicated hall pressure. | April 2026 calibration found positive bias of 0.12 bar. | CAL-PT404-2026-0421

## Calibration_Certificates
Calibration Certificate Register
Certificate metadata and sign-off status.
Certificate | Instrument | Reference standard | Result | Signed by | Approval status | Comment
CAL-FT210-2026-0418 | FT-210 | Portable ultrasonic flow reference UF-07 | PASS with historian scaling correction | I. Dawson, Instrument Engineer | APPROVED | Transmitter itself is within tolerance; historian mapping is wrong.
CAL-PT401-2026-0421 | PT-401 | Deadweight tester DWT-03 | PASS with -0.15 bar correction | I. Dawson, Instrument Engineer | APPROVED | Bias is stable across test points.
CAL-PT404-2026-0421 | PT-404 | Deadweight tester DWT-03 | PASS with -0.12 bar correction | I. Dawson, Instrument Engineer | APPROVED | Bias is stable across test points.
CAL-LT201-2026-0419 | LT-201 | Manual dip and survey benchmark | PASS | I. Dawson, Instrument Engineer | APPROVED | No correction required.